Design of the Distribution Panel of Bhausaheb Mulak Ayurvedic College

Prajwal P. Amrutkar      K.D.K.C.E, Nagpur          prajwal.amrutkar02@gmail.com

Shubham k. Raut            K.D.K.C.E, Nagpur           rautshubham.22.1994@gmail.com

Prof. D.T Korsane         K.D.K.C.E, Nagpur

Abstract – This report discusses about designing the new distribution panel for Bhausaheb Mulak Ayurvedic College involving analysis of the existing (old) distribution panel and the components present. On account of a comprehensive study of the existing distribution panel considering various aspects such as distribution panel rules and standards, improved protection equipments, future load  expansions etc the design of new distribution panel would be done. This report also covers the study of circuit breakers and various components used in distribution panel.

Keywords- Distribution Panel, D-G Set

- INTRODUCTION

Distribution panel are majorly used in order to distribute the incoming power supply to various sub distribution boards and corresponding loads connected to it. In case fault occurs in a distribution panel, trained personnel and special measuring instruments are used for quick and accurate fault location. In order to restore supply at earliest possible time, thus design of the distribution panel should be systematic with respect to certain standards

Distribution boards may be designated for three-phase or single-phase and normal power or emergency power, or designated by use such as distribution panels for supplying other panels, lighting panels for lights, power panels for equipment and receptacles and special uses Since the designing of distribution panel is based upon certain constraints as distribution panel rules and standards, improved protection equipments, future expansions etc a comprehensive data analysis is required

- OBJECTIVE

The main objectives namely are:

1. To analyze the existing distribution panel and components present on the panel.

2. To calculate the load connected to existing distribution panel.

3. To calculate the maximum load demand of the college premises.

4. To design the new distribution panel.

5. To provide a provision of DG Set for uninterrupted power supply.

- EXISTING DISTRIBUTION PANNEL

Distribution boards may be designated for three-phase or single-phase and normal power or emergency power, or designated by use such as distribution panels for supplying other panels, lighting panels for lights, power panels for equipment and receptacles and special uses

Since the designing of distribution panel is based upon certain constraints as distribution panel rules and standards, improved protection equipments, future expansions etc a comprehensive data analysis is required

Incoming line from MSEB 11KV/415V

Fig: Existing Distribution Panel

There is a three and half core 415V incomer cable from SNDL Nagpur coming inside the college premises of about 50sq mm which energizes the entire distribution panel. Only single phase loads are present in the college premises.

Appropriate tapings are taken from the 3phase bus bar in order to feed these single phase loads and also to make sure that adequate optimum load balancing is done amongst all the respective three phases in order to ensure reliability of supply without any unbalance fault phenomenon taking place causing interruption of supply with respect to the place of fault point. It is made sure in the present distribution panel that each and every circuit is provided with neutral path for ensuring that safety parameter are maintained without any issue. The  single phase loads present in the hostel premises also includes 1.5HP motors which are used for pumping water to the overhead water tank from the well. Both these motor is operated by using direct on line starters (DOL starters).

The protection equipments used in the existing distribution are iron cladded triple pole and iron cladded double pole switches (ICTP & ICDP) and simple rewirable fuses. As the existing distribution panel is not an enclosed one, rusting has also taken place to certain extent thus there is always a risk that the metal framework entirely or a part of it may collapse causing interruption of supply or even short circuit in adverse condition.

Also the design of the old distribution panel is not advanced thus it cannot house modern electrical components and related extension accessories for enhancement.

IV. COMPONENTS USED IN DISTRIBUTION PANNEL

- Enclosure

An enclosure is necessary so as to keep the distribution panel isolated and intact from the external atmospheric conditions such as heat, rain, dust, moisture and other foreign interferences. The enclosure should be strong enough to withstand and protect the distribution panel installed inside it, theenclosure should also be painted so as to corrosion

4.2. Busbar

In electrical power distribution, a busbar is a metallic strip or bar (typically copper, brass or aluminium) that conducts electricity within a switchboard, distribution board or other electrical apparatus. Its main purpose is to conduct a substantial current of electricity. Busbars are produced in a variety of shapes such as flat strips, solid bars and rods, solid or hollow tubes, and braided wire. Some of these shapes allow heat to dissipate more efficiently due to their high surface area to cross-sectional area ratio.

[ IS:375 ]

B. Energy Meter

An electricity meter or energy meter is a device that measures the amount of electric energy consumed by a residence, business, or an electrically powered device. They are typically calibrated in billing units, the most common one being the kilowatt hour [kWh].           The energy meter is the first component to which the incomer cables are connected. The energy meter further also has many types, the trivector energy meters are capable of representing the reactive power consumption which is thus of an advanced type as compared to general service energy meters

C.CTP & ICDP Switches

The ICTP & ICDP stand for iron cladded triple/double pole switches. These are the manually operated protection components. These switches are placed before the fuses in the distribution panel circuitry. Before installing these switches the current rating is determined previously based upon which there installation is done. In case of abnormal condition these switches melt down on account of excess current flow.

D. Starter

An electrical starter is basically a protection device that limits the heavy starting current drawn by the motor ensuring that currents stays below a safe value and gradually cuts off  after the motor attains a speed greater than 85% of its rated speed. The staters used in the hostel premises are DOL starters since the motors present are of 5HP each and also these starters are less costlier, easy to maintain and controlling mechanism is also simple

4.6. Fuses

A fuse is a type of low resistance resistor that acts as a sacrificial device to provide overcurrent protection, of either the load or source circuit. Its essential component is a metal wire or strip that melts when too much current flows through it, interrupting the circuit that it connects. Short circuits, overloading, mismatched loads, or device failure are the prime reasons for excessive current. Fuses are an alternative to circuit breakers. A fuse interrupts excessive current so that further damage by overheating or fire is prevented. Rewirable cartridge type fuses are used in the existing old distribution panel.

E. MCB & MCCB

MCBs or Miniature Circuit Breakers are electromechanical devices which protect an electrical circuit from an overcurrent. The overcurrent, in an electrical circuit, may result from short circuit, overload or faulty design. An MCB is a better alternative to a Fuse since it does not require replacement once an overload is detected. Unlike fuse, an MCB can be easily reset and thus offers improved operational safety and greater convenience without incurring large operating cost.

F. Cables

An electrical cable comprises two or more wires running side by side and bonded, twisted, or braided together to form a single assembly, the ends of which can be connected to devices, enabling the transfer of electrical power from one point to the other. The types of cable used precisely depends upon the type of electrical load connected andthe power which is to be transferred taking into account the current ratings.

[IS:3961 (PART II) – 1967]

V. LOAD CALCULATIONS

Even though the installation of a distribution panel is based upon many essential parameters, the calculation relating to the load have a significant importance since we need to know that what amount of  load is to fed by the distribution panel which is going to be designed.

The old distribution panel currently feeds about 14-15KW of connected load of  the college premises. As the old distribution panel was built about twenty five years ago, its design is thereby not much advanced for installing new protection equipments which are these days almost essential in order to ensure smooth and uninterrupted supply of electrical power. Thus there comes a need to design a new panel which would host of modern protection equipments and would be capable of incorporating any kind of future expansions as and when required   Calculation of the connected load of the Bhausaheb Mulak Ayurvedic College  can be tabulated as:

Table:  Ground Floor load

| Table : 1st Floor load Sr.no. | EQUIPMENTS | RATINGS | No. OF EQUIPMENTS | TOTAL LOAD |
| --- | --- | --- | --- | --- |
| 1. | Fans | 60W | 45 | 2700W |
| 2. | Tube Lights | 40W | 32 | 1280W |
| 3. | Bulbs | 40W | 14 | 560W |
| 4. | Power Socket with switch | 100W | 36 | 3600W |
| 5. | A.C | 4000W | 2 | 8000W |
| 6. | Water Pump | 1119W | 1 | 1119W |
|  |  |  | TOTAL | 17259W |

| Sr.NO | EQUIPMENTS | RATINGS | No. OF EQUIPMENTS | TOTAL LOAD |
| --- | --- | --- | --- | --- |
| 1. | Fans | 80W | 45 | 3600W |
| 2. | Tube-lights | 40W | 32 | 1280W |
| 3. | CCTV | 20W | 2 | 40W |
| 4. | Refrigerators | 400W | 1 | 400W |
| 5. | Bulbs | 40W | 3 | 120W |
|  |  |  | TOTAL | 5440W |

Table :  2nd Floor load

| S.NO | EQUIPMENTS | RATINGS | No. OF EQUIPMENTS | TOTAL LOAD |
| --- | --- | --- | --- | --- |
| 1. | Fans | 80W | 45 | 3600W |
| 2. | Tube-lights | 40W | 32 | 1280W |
| 3. | Gysers | 1500W | 1 | 1500W |
| 4. | CFLS | 12W | 6 | 72W |
| 5. | A.C | 4000W | 2 | 8000W |
|  |  |  | TOTAL | 14452W |

On calculation these floors on cumulative basis add up to a total load of about 19 KW for ground floor , about 6KW for 1st floor and about 14KW  for 2nd floor which is also required to be considered while designing the new layout of distribution panel which includes  the load of 3rd floor too. After considering the entire load requirement summing up of the Ayurvedic College  and  all the floors in that particular complex, the total maximum load demand ranges to somewhere around 40KW on cumulative basis of calculation .

VI. NEW DISTRIBUTION PANNEL

The single line diagram of the old existing distribution panel itself indicates the old protection components used ie the ICTP and the ICDP switches, the protection components used are not much advanced as compared to the modern protection componentsavailable commonly in the market these days. Also the do not offer the service offered by these old equipments is poor as compared to the new devices available such as MCB and MCCB.

As seen from the single line diagram above, modern and advanced protection components like MCB and MCCB have been used in order to increase the margin of safety also increasing the reliability of supply and fault clearing ability thereby making an overall enhancement in the functioning and serving the purpose in a better and efficient way.

VII. FURTHER SUGGESTED WORK

After certain typical comprehensive study and  load calculations we can also put forward an idea of installing a DG Set for the Ayurvedic college. Installing a DG Set would thereby ensure that the supply of electricity would be available as and when required. The average loading of the college premises comes out to be 14-15 KW for which a DG Set of 18KVA would be sufficient.

REFERENCES

- V.K Jain & Amitabh Bajaj ,“A Textbook of Design of Electrical Installations”; Laxmi Publications Pvt. Limited,1993.1st Edition.

- J.B. Gupta, “A Course in Electrical Installation, Estimating & Costing”; Published by S.K Kataria & Sons, 9th Edition.

- A.S.Pabla, “Electrical Power Distribution System” ;Tata McGraw-Hill, 5th Edition.

- Indian Electricity Regulation, 1956.

Incoming line from MSEB 11KV/415V